2020/3/24: 1:30PM

Installed portable blackbody to Tube Alloy unit.

Checked at 850F blackbody and pyrometers, both within less than 1% variation – good

Notice a difference on HMI and Pyrometer

Set to 1000F to verify the gap

Pyrometer 2: 1011F BB 999F HMI: 951Fand

Pyrometer 1: 1006F BB 1000F HMI: 947Fand

Adjusted process parameters to 20mA signal to 1440 and dif went to less than 2F